|  | U.S. Department of Labor |  |
| --- | --- | --- |
|  | Occupational Safety & Health Administration Top of Form |  |
|  | www.osha.gov |  | MyOSHA[skip navigational links] | Search | Advanced Search ¦ A-Z Index | Bottom of Form |

Construction > Construction Outreach TOC > Common Fire Extinguishing Agents

Construction Safety and Health Outreach Program U.S. Department of Labor OSHA Office of Training and Education May 1996 Common Fire Extinguishing Agents

Carbon dioxide Dry chemical Multipurpose dry chemical Halon 1301 Halon 1211

WATER

Removes heat Effective on Class A fires Inexpensive Plentiful Non-toxic Disadvantages: Conducts electricity May spread Class B fires Freezes in cold climates May carry pollutants as run-off water

CARBON DIOXIDE (CO2)

Reduces oxygen to less than 15% Effective on Class B and C fires No residue Relatively inert Disadvantages: Generally >35% concentration by volume required for total flooding system Toxic to humans at >4% by volume Not the best agent for smoldering deep-seated fires (maintain concentration for >20 minutes) Dissipates rapidly - allows reflash Has a cooling/chilling effect on some electronic components Vapor density = 1.5 (collects in pits and low areas)

DRY CHEMICAL

Interrupts chemical reactions Sodium bicarbonate (baking soda) Very effective on Class B and C fires Not considered toxic Disadvantages: Leaves a residue Obscures vision Not good on deep-seated Class A fires Absorbs moisture and may "cake" within container May be irritating Nozzle pressure may cause burning liquids to splash

MULTIPURPOSE DRY CHEMICAL Interrupts chemical reactions Ammonium phosphate Effective on Class A, B, and C fires Non-conductive Disadvantages: Obscures vision More irritating than ordinary dry chemical Nozzle pressure may cause burning liquids to splash

HALON TERMINOLOGY

Halon 104: Carbon tetrachloride (CCl4) Halon 1211: Bromochlorodifluoromethane (CBrClF2) Halon 1301: Bromotrifluoromethane (CBrF3)

C F Cl Br 1 0 4 - 1 2 1 1 1 3 0 1

> HALON 1301

Interrupts chemical reactions Bromotrifluoromethane Effective on Class A, B, and C fires Not acutely toxic at <10% by volume Generally used at <7% by volume No residue No chilling effect on electronic parts and components Disadvantages: Acutely toxic at >10% by volume (anesthetic and cardiac effects) Delayed effects and effects of chronic exposure not well known Toxic decomposition products are generated by fire Vapor density = 5 (collects in pits and low areas) Production restricted per Montreal Protocol due to depletion of ozone layer

HALON 1301 DECOMPOSITION PRODUCTS

Hydrogen fluoride (HF) Hydrogen bromide (HBr) Bromine (Br2) Carbonyl Fluoride (COF2) Carbonyl Bromide (COBr2)

HALON 1211

Interrupts chemical reactions Bromochlorodifluoromethane Effective on Class A, B, and C fires No residue May be sprayed (Boiling Point = 25oF) Used in portable fire extinguishers Disadvantages: Acutely toxic at >4% by volume (dizziness, impaired coordination and cardiac effects) Must be used at >5% by volume Toxic decomposition products are generated by fire Vapor density = 5.7 (collects in pits and low areas) Production restricted per Montreal Protocol due to depletion of ozone layer

HALON 1211 DECOMPOSITION PRODUCTS

Hydrogen bromide (HBr) Hydrogen chloride (HCl) Hydrogen fluoride (HF) Bromine (Br2) Chlorine (Cl2) Fluorine (F2) Carbonyl bromide (COBr2) Carbonyl chloride (COCl2) Carbonyl fluoride (COF2)

| Back to Top www.osha.gov | www.dol.gov |
| --- | --- |
| Contact Us ¦ Freedom of Information Act ¦ Information Quality ¦ Customer Survey Privacy and Security Statement ¦ Disclaimers |
| Occupational Safety & Health Administration 200 Constitution Avenue, NW Washington, DC 20210 |  |  |